## Physical Treatment
Aspect |  |  |  | Line No. | Physical / mechanical treatment
[5 empty] | Screening | [5 empty] | Sedimentation
[5 empty] | With precipitation / flocculation |  | Without precipitation / flocculation |  | Micro-sieving 10 µm |  | With precipitation / flocculation |  | Without flocculation
Health risk | Operating personnel water processing facility |  |  | 1 | high (handling of chemicals) | 25 | medium | 25 | medium | 35 | high (handling of chemicals) | 28 | medium | 28
| Users of reused water |  |  | 2 | low (only as pre-treatment stage) | 25 | low (only as pre-treatment stage) | 25 | low (requires disinfection) | 27 | low (only as pre-treatment stage) | 28 | low (only as pre-treatment stage) | 28
Economic efficiency | Investment costs | Footprint requirement |  | 3 | low | 25 | low | 25 | low | 27 | low (0.04-0.06 m2/PT) | 6 | low (0.02-0.04 m2/PT) | 6
|  | Structural engineering |  | 4 | medium (400-1000 €/(m³/h) + flocculation) | 2 | low (400-1000 €/(m³/h)) | 2 | low | 27 | medium (250-1000 €/PT settling tank + 1-80 €/PT precipitation) | 3 | medium (250-1000 €/PT for settling tank) | 3
|  | Mechanical engineering |  | 5 | low | 25 | low | 25 | medium | 27 | low | 34 | low | 34
|  | E+MCR technology |  | 6 | low | 25 | low | 25 | low | 27 | low | 34 | low | 34
| Operating costs | Personnel requirement / costs |  | 7 | low | 25 | low | 25 | medium | 35 | low | 34 | low | 34
|  | Energy requirement / costs |  | 8 | medium (0.0117-0.017 kWh/m3) | 27 | medium (0.009-0.013 kWh/m3) | 27 | medium / high (fine sieve 250 µm: 0.083 kWh/m3) | 35 | low (~ 0.002 kWh/m³) | 5 | low (~ 0.001 kWh/m³) | 5
|  | Disposal of residues |  | 9 | high | 25 | medium | 25 | low | 27 | high | 34 | medium | 34
|  | Operating supplies (precipitant etc.) |  | 10 | high | 25 | low (no operating supplies) | 25 | low | 27 | high | 34 | low (no operating supplies) | 34
|  | Preventive maintenance costs |  | 11 | low | 25 | low | 25 | low | 27 | low | 34 | low | 34
Effects on the environment through operation of the facility | CH4 emission |  |  | 12 | none | 25 | none | 25 | none | 27 | low (only with long sedimentation times slight methane formation through anaerobic degradation process possible) | 30 | low (only with long sedimentation times slight methane formation through anaerobic degradation process possible) | 30
| Odour nuisance |  |  | 13 | high | 29 | high | 29 | low | 27 | low | 29 | medium | 29
| Sounds / noisiness |  |  | 14 | low | 29 | low | 29 | low | 27 | low | 29 | low | 29
| Aerosols |  |  | 15 | low | 29 | low | 29 | medium | 27 | low | 29 | low | 29
| Insects (worms, flies, etc.) |  |  | 16 | high | 29 | high | 29 | low | 27 | medium | 29 | low | 29
Requirements on operating personnel | Operability /operational expenditure |  |  | 17 | medium | 31 | low | 25 | medium | 31 | medium | 31 | low | 31
| Preventive maintenance expenditure |  |  | 18 | medium | 31 | low | 25 | medium | 31 | medium | 31 | low | 31
| Required training for operating personnel |  |  | 19 | medium | 29 | low | 29 | medium (trained personnel required) | 27 | medium | 29 | low | 29
Plant technology | Degree of mechanization |  |  | 20 | low / medium | 25 | low | 25 | high | 27 | medium | 27 | low | 27
| Robustness |  |  | 21 | high | 25 | high | 25 | medium | 27 | medium | 27 | high | 27
| Process stability |  |  | 22 | high | 25 | high | 25 | medium | 27 | high | 27 | high | 27
| Ability to influence the discharge quality operationally |  |  | 23 | medium | 25 | low | 31 | low | 31 | medium | 31 | low | 31
| Discharge quality (treatment performance) | COD / BOD elimination |  | 24 | medium (maximum 60 %) | 25 | low (maximum 25 %) | 25 | low (> 10 % or < 60 mg/l) | 27 | medium / high (55-75 % COD; 45-80 % BOD) | 6 | medium (25-35 % COD; 30-35 % BOD) | 6
|  | SS reduction |  | 25 | high (maximum 95 %) | 25 | high (85 %) | 25 | medium (> 30 % or < 10 mg/l) | 27 | medium / high (60-90 %) | 6 | medium (55-65 %) | 6
|  | Nutrient elimination | Ammonium | 26 | low (ca. 10 %) | 34 | low (ca. 10 %) | 34 | low | 27 | low (<30 %) | 6 | low (< 30 %) | 6
|  |  | Nitrate | 27 | no influence (0 %) | 25 | no influence (0 %) | 25 | low | 27 | no influence (0 %) | 34 | no influence (0 %) | 3
|  |  | Phosphorus | 28 | high | 25 | low (< 10 %) | 25 | low | 27 | high (75-90 %) | 6 | medium / low (< 35 %) | 6
|  | Reductions of pathogens | Viruses | 29 | low | 34 | low | 34 | no detail | 27 | low (1 - 2 log steps) | 1 | low (0 - 1 log steps) | 1
|  |  | Bacteria | 30 | low | 34 | low | 34 | no detail | 27 | low (1 - 2 log steps) | 1 | low (0 - 1 log steps) | 1
|  |  | Protozoa | 31 | low | 34 | low | 34 | no detail | 27 | low (1 - 2 log steps) | 1 | low (0 - 1 log steps) | 1
|  |  | Helminths | 32 | low | 34 | low | 34 | high (helminths eggs up to 100 % using 10 µm mesh) | 35 | medium (1 - 3 log steps) | 1 | low (0 - < 1 log steps) | 1
|  | Colour / odour |  | 33 | no influence | 25 | no influence | 25 | no influence | 27 | low with longer sedimentation times (odour through anaerobic degradation processes possible) | 30 | low with longer sedimentation times (odour through anaerobic degradation processes possible) | 30
|  | Residual turbidity |  | 34 | medium | 35 | high | 35 | low | 27 | medium | 35 | high | 35
|  | Salting up due to process |  | 35 | medium (salting through precipitation chemicals) | 25 | no influence | 25 | no influence | 27 | medium | 35 | no influence | 30
| Accumulation of residues |  |  | 36 | medium (country-specific; 15-70 l/(PT·a)) | 27 | medium (country-specific; 15-60 l/(PT·a)) | 27 | low | 27 | high (730-2500 l/(PT·a) un-stabilised, liquid or 40-110 l/(PT·a) dewatered sludge) | 6 | low (330-730 l/(PT·a) un-stabilised, liquid or 15-40 l/(PT·a) dewatered sludge) | 6
Irrigation technology | Root irrigation |  |  | 37 | not suitable | 25 | not suitable | 25 | suitable | 27 | not suitable | 10 | not suitable | 10
| Trickling irrigation |  |  | 38 | not suitable | 25 | not suitable | 25 | suitable (requires disinfection, virus and bacteria can pass the 10 µm mesh) | 35 | not suitable | 10 | not suitable | 10
| Sprinkler / spray systems |  |  | 39 | suitable (requires disinfection) | 25 | not suitable | 25 | suitable (ditto) | 35 | suitable (requires disinfection) | 10 | suitable (requires disinfection) | 10
| Flooding |  |  | 40 | suitable | 25 | suitable | 25 | suitable (ditto) | 35 | suitable (requires disinfection, virus and bacteria can pass the 10 µm mesh) | 35 | suitable | 10
Types of usage | Agricultural irrigation |  |  | 41 | possible (requires disinfection) | 35 | not recommended | 29 | recommended (ditto) | 35 | possible (requires disinfection) | 35 | possible (requires disinfection) | 35
| Process water (e.g., toilet flushing) |  |  | 42 | not recommended | 25 | not possible | 25 | possible (ditto) | 35 | not recommended | 29 | not possible | 29
| Inner-city usage (e.g., irrigation, water for fire-fighting) |  |  | 43 | not recommended | 25 | not possible | 25 | possible (ditto) | 35 | not recommended | 29 | not possible | 29
| Forestry irrigation |  |  | 44 | possible (requires disinfection) | 35 | possible (requires disinfection) | 35 | recommended (ditto) | 35 | possible (requires disinfection) | 35 | possible (requires disinfection) | 35

## Ponds
Aspect |  |  |  | Line No. | Wastewater ponds | [5 empty] | Wastewater storage and treatment tank
[5 empty] | Aerated / aerobic with sedimentation pond |  | Facultative / anaerobic pond |  | Downstream polishing pond
Health risk | Operating personnel water processing facility |  |  | 1 | low | 26,33 | low | 26,33 | low | 26,33 | low | 26,33
| Users of reused water |  |  | 2 | medium (requires disinfection) | 26,33 | medium (requires disinfection) | 26,33 | medium (requires disinfection) | 26,33 | low (with long retention time) | 26,33
Economic efficiency | Investment costs | Footprint requirement |  | 3 | high (0.25-0.5 m2/PT) | 6 | high (1.2-3.0 m2/PT) | 6 | high (3.0-5.0 m2/PT) | 6 | high | 6
|  | Structural engineering |  | 4 | low (300-1000 €/PT) | 26,33 | low (300-1000 €/PT) | 26,33 | low (300-1000 €/PT) | 26,33 | medium | 26,33
|  | Mechanical engineering |  | 5 | low | 2 | low | 2 | low | 26,33 | low | 26,33
|  | E+MCR technology |  | 6 | low | 2 | low | 2 | low | 26,33 | low | 26,33
| Operating costs | Personnel requirement / costs |  | 7 | low | 4 | low | 4 | low | 34 | low | 26,33
|  | Energy requirement / costs |  | 8 | medium | 33 | low | 33 | low | 33 | low | 26,33
|  | Disposal of residues |  | 9 | medium | 26,33 | medium | 26,33 | low | 26,33 | low | 26,33
|  | Operating supplies (precipitant etc.) |  | 10 | low (no operating supplies) | 26,33 | low (no operating supplies) | 26,33 | low (no operating supplies) | 26,33 | low (no operating supplies) | 26,33
|  | Preventive maintenance costs |  | 11 | low | 26,33 | low | 26,33 | low | 26,33 | low | 26,33
Effects on the environment through operation of the facility | CH4 emission |  |  | 12 | medium (methane formation in settling areas trough anaerobic degradation process) | 26,33 | high (considerable methane formation through anaerobic degradation process) | 26,33 | low (possible methane formation through degradation of residual loads and sludge) | 26,33 | high (considerable methane production through anaerobic degradation processes) | 26,33
| Odour nuisance |  |  | 13 | low | 26,33 | high (dependent on operation) | 26,33 | low | 26,33 | low | 26,33
| Sounds / noisiness |  |  | 14 | medium (dependent on aeration facility) | 26,33 | none | 26 | none | 26 | none | 26
| Aerosols |  |  | 15 | medium (dependent on aeration facility) | 26,33 | low | 26,33 | low | 26,33 | low | 26,33
| Insects (worms, flies, etc.) |  |  | 16 | high (mosquitos) | 26,33 | high (mosquitos) | 26,33 | high (mosquitos) | 26,33 | high (mosquitos) | 26,33
Requirements on operating personnel | Operability /operational expenditure |  |  | 17 | low | 26,33 | low | 26,33 | low | 26,33 | low | 26,33
| Preventive maintenance expenditure |  |  | 18 | low | 26,33 | low | 26,33 | low | 26,33 | low | 26,33
| Required training for operating personnel |  |  | 19 | low | 26,33 | low | 26,33 | low | 26,33 | low | 26,33
Plant technology | Degree of mechanization |  |  | 20 | low | 26,33 | low | 26,33 | low | 26,33 | low | 26,33
| Robustness |  |  | 21 | high | 26,33 | high | 26,33 | high | 26,33 | high | 26,33
| Process stability |  |  | 22 | high | 26,33 | high | 26,33 | high | 26,33 | high | 26,33
| Ability to influence the discharge quality operationally |  |  | 23 | low | 26,33 | low | 26,33 | low | 26,33 | low | 26,33
| Discharge quality (treatment performance) | COD / BOD elimination |  | 24 | medium / high (65-80 % COD; 75-85 % BOD) | 6 | medium / high (65-80 % COD; 75-85 % BOD) | 6 | low (reduction residual loads / balancing of effluent peaks) | 26,33 | low (reduction residual loads / balancing of effluent peaks) | 10
|  | SS reduction |  | 25 | high (70-80 %) | 6 | high (70-80 %) | 6 | low (reduction residual loads / balancing of effluent peaks) | 26,33 | low (reduction residual loads / balancing of effluent peaks) | 10
|  | Nutrient elimination | Ammonium | 26 | low (< 30 %) | 6 | medium (< 50 %) | 6 | low (reduction residual loads / balancing of effluent peaks) | 26,33 | low (reduction residual loads / balancing of effluent peaks) | 10
|  |  | Nitrate | 27 | low (< 30 % Ntot) | 6 | medium (< 60 % Ntot) | 6 | low (reduction residual loads / balancing of effluent peaks) | 26,33 | low (reduction residual loads / balancing of effluent peaks) | 10
|  |  | Phosphorus | 28 | medium / low (< 35 %) | 6 | medium / low (< 35 %) | 6 | low (reduction residual loads / balancing of effluent peaks) | 26,33 | low (reduction residual loads / balancing of effluent peaks) | 10
|  | Reductions of pathogens | Viruses | 29 | low (1 - 2 log steps, dependent on retention time) | 1 | high (1 - 4 log steps, dependent on retention time) | 1 | high (1 - 4 log steps, dependent on retention time) | 1 | high (1 - 4 log steps, dependent on retention time) | 1
|  |  | Bacteria | 30 | low (1 - 2 log steps, dependent on retention time) | 1 | high (1 - 6 log steps, dependent on retention time) | 1 | high (1 - 6 log steps, dependent on retention time) | 1 | high (1 - 6 log steps, dependent on retention time) | 1
|  |  | Protozoa | 31 | low (0 - 1 log steps, dependent on retention time) | 1 | high (1 - 4 log steps, dependent on retention time) | 1 | high (1 - 4 log steps, dependent on retention time) | 1 | high (1 - 4 log steps, dependent on retention time) | 1
|  |  | Helminths | 32 | medium (1 - 3 log steps, dependent on retention time) | 1 | medium (1 - 3 log steps, dependent on retention time) | 1 | medium (1 - 3 log steps, dependent on retention time) | 1 | medium (1 - 3 log steps, dependent on retention time) | 1
|  | Colour / odour |  | 33 | medium (colouration due to algae and bacteria) | 26,33 | high (colouration through algae and bacteria / odour through anaerobic degradation processes) | 26,33 | medium (colouration due to algae and bacteria) | 26,33 | medium (colouration due to algae formation and bacteria) | 26,33
|  | Residual turbidity |  | 34 | medium | 26,33 | medium | 26,33 | medium | 26 | low | 26,33
|  | Salting up due to process |  | 35 | medium (danger of salting uo through evaporation) | 26,33 | medium (danger of salting uo through evaporation) | 26,33 | medium (danger of salting uo through evaporation) | 26,33 | medium (danger of salting uo through evaporation) | 26,33
| Accumulation of residues |  |  | 36 | medium (periodic sludge clearance) | 26,33 | medium (periodic sludge clearance) | 26,33 | low (periodic sludge clearance) | 26,33 | low (periodic sludge clearance) | 26,33
Irrigation technology | Root irrigation |  |  | 37 | suitable (requires filtration) | 10 | suitable (requires filtration) | 10 | suitable (requires filtration) | 10 | suitable (requires filtration) | 10
| Trickling irrigation |  |  | 38 | suitable (requires filtration) | 10 | suitable (requires filtration) | 10 | suitable (requires filtration) | 10 | suitable (requires filtration) | 10
| Sprinkler / spray systems |  |  | 39 | less suitable (requires disinfection) | 10 | suitable | 10 | suitable | 10 | suitable | 10
| Flooding |  |  | 40 | suitable | 10 | suitable | 10 | suitable | 10 | suitable | 10
Types of usage | Agricultural irrigation |  |  | 41 | possible | 26,33 | possible | 26,33 | possible | 26,33 | possible | 26,33
| Process water (e.g., toilet flushing) |  |  | 42 | not recommended | 26,33 | not recommended | 26,33 | not recommended | 26,33 | not recommended | 26,33
| Inner-city usage (e.g., irrigation, water for fire-fighting) |  |  | 43 | not recommended | 26,33 | not recommended | 26,33 | not recommended | 26,33 | not recommended | 26,33
| Forestry irrigation |  |  | 44 | possible | 26,33 | possible | 26,33 | possible | 26,33 | possible | 26,33

## UASB_ABR_AS_TF_CW
Aspect |  |  |  | Line No. | UASB (upflow anaerobic sludge blanket reactor) |  | ABR (anaerobic baffled reactor) |  | Activated sludge process |  |  |  | Trickling filter |  | Constructed wetlands
[9 empty] | C removal |  | Nutrient removal
Health risk | Operating personnel water processing facility |  |  | 1 | low | 28 | low | 37 | low | 28 | high (handling of chemicals) | 28 | low | 28 | low | 28
| Users of reused water |  |  | 2 | low (only as pre-treatment stage) | 28 | low (operated as pre-treatment) | 37 | medium (requires disinfection) | 28 | medium (requires disinfection) | 28 | medium (requires disinfection) | 28 | medium (requires disinfection) | 28
Economic efficiency | Investment costs | Footprint requirement |  | 3 | low (0.03-0.1 m2/PT) | 6 | low (0.05-0.07 m2/PT) | 37 | low (0.12-0.25 m2/PT) | 6 | low (0.12-0.25 m2/PT) | 6 | low (0.12-0.3 m2/PT) | 6 | high (3-5 m2/PT) | 6
|  | Structural engineering |  | 4 | medium | 26 | low | 41 | medium (100-800 €/PT) | 2 | medium (200-900 €/PT) | 2 | medium (200-600 €/PT) | 2 | high (1000-2000 €/PT) | 24
|  | Mechanical engineering |  | 5 | medium | 30 | none | 37 | medium (40-80 €/PT) | 2 | medium (40-80 €/PT) | 2 | low | 2 | low | 24
|  | E+MCR technology |  | 6 | medium | 30 | none | 37 | high | 2 | high | 2 | low | 2 | low | 24
| Operating costs | Personnel requirement / costs |  | 7 | low | 30 | low | 41 | medium (5-10 €/(PT·a)) | 8 | medium (5-10 €/(PT·a)) | 8 | low | 4,9 | low (50-130 €/(PT·a)) | 24
|  | Energy requirement / costs |  | 8 | low | 30 | low | 25 | high (~0.110 kWh/m³) | 5 | high (~0.190 kWh/m³) | 5 | medium (~0.085 kWh/m³) | 5
|  | Disposal of residues |  | 9 | low | 30 | low | 41 | medium (10-20 €/(PT·a)) | 8 | medium (10-20 €/(PT·a)) | 8 | low | 4,9
|  | Operating supplies (precipitant etc.) |  | 10 | low (no operating supplies) | 30 | low (no operating supplies) | 25 | medium (1-2.5 €/(PT·a)) | 8 | medium (1-2.5 €/(PT·a)) | 8 | low | 4,9
|  | Preventive maintenance costs |  | 11 | low | 32 | low | 37 | medium (2.5-5 €/(PT·a)) | 8 | medium (2.5-5 €/(PT·a)) | 8 | low | 4,9
Effects on the environment through operation of the facility | CH4 emission |  |  | 12 | high (methane load dissolved in the treated water (the more, the higher the temperature) evaporates) | 30 | high (gas phase and dissolved in effluent) | 41 | none | 30 | none | 30 | none (only if air flow insufficient possible formation of anaerobic zones with methane development) | 30 | low (formation of anaerobic zones with methane development possible) | 26
| Odour nuisance |  |  | 13 | medium | 25 | medium | 25 | medium | 29 | low | 29 | medium | 30 | low | 30
| Sounds / noisiness |  |  | 14 | low | 30 | low | 25 | medium / high (dependent on plant technology) | 29 | medium / high (dependent on plant technology) | 29 | none | 26 | none | 26
| Aerosols |  |  | 15 | low | 30 | low | 25 | low / high (dependent on plant technology) | 29 | low / high (dependent on plant technology) | 29 | low | 30 | low | 30
| Insects (worms, flies, etc.) |  |  | 16 | low | 30 | low | 41 | low | 29 | low | 29 | high | 30 | high | 30
Requirements on operating personnel | Operability /operational expenditure |  |  | 17 | medium | 30 | low | 37 | medium | 31 | high | 31 | medium | 30 | low | 30
| Preventive maintenance expenditure |  |  | 18 | medium | 30 | low | 37 | medium | 31 | high | 31 | medium | 30 | low (periodic cutting of the plants) | 30
| Required training for operating personnel |  |  | 19 | medium | 30 | low | 37 | medium | 29 | high | 29 | medium | 30 | low | 30
Plant technology | Degree of mechanization |  |  | 20 | low | 27 | low | 37 | high | 27 | high | 27 | medium | 30 | low | 27
| Robustness |  |  | 21 | low | 27 | medium | 25 | high | 27 | high | 27 | high | 27 | low\medium | 27
| Process stability |  |  | 22 | low | 27 | medium | 38 | high | 27 | high | 27 | high | 27 | high | 27
| Ability to influence the discharge quality operationally |  |  | 23 | medium | 30 | low | 37 | high | 30 | high | 30 | medium | 30 | low | 30
| Discharge quality (treatment performance) | COD / BOD elimination |  | 24 | medium / high (50 to 85-95 %) | 30 | medium / high (60-80 %) | 38 | high (80-90 % COD; 85-93 % BOD) | 6 | high (80-90 % COD; 85-93 % BOD) | 6 | high (70-90 % COD; 80-93 BOD) | 6 | high (75-85 % COD; 80-90 % BOD) | 6
|  | SS reduction |  | 25 | medium / high (65-80 %) | 6 | medium / high (60-80 %) | 38 | high (87-93 %) | 6 | high (87-93 %) | 6 | high (87-93 %) | 6 | high (87-93 %) | 6
|  | Nutrient elimination | Ammonium | 26 | low | 25 | low | 39 | low (ca. 20 %) | 3 | high (> 80 %) | 6 | medium / high (50-85 %) | 6 | medium / high (40-98 % with seasonal variations) | 29
|  |  | Nitrate | 27 | low | 25 | low | 39 | no effect (0 %) | 3 | high (ca. 80 %) | 34 | medium (< 60 % Ntot) | 6 | low (0-17 %) | 24
|  |  | Phosphorus | 28 | low | 25 | low | 39 | low (30 % w/o precipitation) / high (ca. 90 % with precipitation) | 3 | low (30 % w/o precipitation) / high (ca. 90 % with precipitation) | 3 | medium / low (< 35 % only with precipitation) | 4,9 | medium / high (30-95 % depending on age) | 29
|  | Reductions of pathogens | Viruses | 29 | low (0 - 1 log steps) | 1 | low (1 - 2 log steps) | 39 | low (0 - 2 log steps) | 1 | low (0 - 2 log steps) | 1 | low (0 - 2 log steps) | 1 | low (1 - 2 log steps) | 1
|  |  | Bacteria | 30 | low (0.5 - 1.5 log steps) | 1 | low (< 1 log step) | 39 | low (1 - 2 log steps) | 1 | low (1 - 2 log steps) | 1 | low (1 - 2 log steps) | 1 | medium / low (0.5 - 3 log steps) | 1
|  |  | Protozoa | 31 | low (0 - 1 log steps) | 1 | low (< 1 log step, inferred from information on bacteria) | 39 | low (0 - 1 log steps) | 1 | low (0 - 1 log steps) | 1 | low (0 - 1 log steps) | 1 | low (0.5 - 2 log steps) | 1
|  |  | Helminths | 32 | low (0.5 - 1 log steps) | 1 | low (1 log step) | 39 | low (1 - < 2 log steps) | 1 | low (1 - < 2 log steps) | 1 | low (1 - 2 log steps) | 1 | medium (1 - 3 log steps) | 1
|  | Colour / odour |  | 33 | high (formation of odour substances due to anaerobic degradation) | 30 | high (formation of odour substances due to anaerobic degradation) | 25 | low (with correct operation) | 30 | low (with correct operation) | 30 | low (possible formation of odour substances under anaerobic conditions) | 30 | low (possible formation of odour substances under anaerobic conditions) | 30
|  | Residual turbidity |  | 34 | medium | 30 | medium | 41 | medium | 26 | medium | 34 | medium | 30 | medium | 30
|  | Salting up due to process |  | 35 | no effect | 30 | no effect | 41 | low | 30 | medium (salting up due to precipitation chemicals for P removal) | 30 | low (risk of salting up by precipitant or water evaporation only with higher recirculation rate, strong sunrays, lower air humidity) | 30,34 | low (risk of salting up by evapotranspiration via the plants) | 30
| Accumulation of residues |  |  | 36 | low (70-220 l/(PT·a) unstabi-lized, liquid or 10-35 l/(PT·a) dewatered sludge) | 6 | low (< 15 l/(PT·a) settled sludge) | 40 | high (1100-3000 l/(PT·a) unstabi-lized, liquid or 35-90 l/(PT·a) dewatered sludge | 6 | high (1100-3000 l/(PT·a) unstabilized, liquid or 35-90 l/(PT·a) dewatered sludge) | 6 | medium (360-1900 l/(PT·a) unstabilized, liquid sludge or 35-80 l/(PT·a) dewatered sludge) | 6 | medium / high (plant cutting) | 30
Irrigation technology | Root irrigation |  |  | 37 | not relevant (pre-treatment only) | 10 | not relevant (pre-treatment only) | 25 | suitable (requires filtration) | 10 | suitable (requires filtration) | 10 | less suitable (requires filtration) | 10 | less suitable (requires filtration) | 10
| Trickling irrigation |  |  | 38 | not relevant (pre-treatment only) | 10 | not relevant (requires post treatment) | 41 | suitable (requires filtration) | 10 | suitable (requires filtration) | 10 | less suitable (requires filtration) | 10 | less suitable (requires filtration) | 10
| Sprinkler / spray systems |  |  | 39 | not relevant (pre-treatment only) | 10 | not relevant (requires post treatment) | 41 | suitable (requires disinfection) | 10 | suitable (requires disinfection) | 10 | suitable (requires disinfection) | 10 | suitable (requires disinfection) | 10
| Flooding |  |  | 40 | not relevant (pre-treatment only) | 10 | not relevant (requires post treatment) | 41 | suitable | 10 | suitable | 10 | suitable | 10 | suitable | 10
Types of usage | Agricultural irrigation |  |  | 41 | not recommended | 30 | not recommended | 41 | recommended | 29 | recommended | 29 | possible | 30 | possible | 30
| Process water (e.g., toilet flushing) |  |  | 42 | not possible | 30 | not possible | 41 | not recommended | 29 | possible | 29 | not recommended | 30 | not recommended | 30
| Inner-city usage (e.g., irrigation, water for fire-fighting) |  |  | 43 | not possible | 30 | not possible | 41 | not recommended | 29 | possible | 29 | not recommended | 30 | not recommended | 30
| Forestry irrigation |  |  | 44 | possible | 30 | possible | 41 | recommended | 29 | recommended | 29 | possible | 30 | possible | 30

## Filtration_Precipitation
Aspect |  |  |  | Line No. | Filtration (downstream) | [5 empty] | Precipitation / flocculation (downstream) |  | Membrane technology
[5 empty] | Rapid sand filtration (coarse grain) |  | Slow sand filtration |  | Dual-media filtration |  |  |  | UF / MF (e.g., MBR) |  | NF / RO
Health risk | Operating personnel water processing facility |  |  | 1 | low | 28 | low | 28 | low | 28 | high (handling of chemicals) | 28 | high (handling of chemicals) | 28 | high (handling of chemicals) | 28
| Users of reused water |  |  | 2 | medium (requires disinfection) | 28 | medium (requires disinfection) | 28 | medium (requires disinfection) | 28 | medium (requires disinfection) | 28 | low | 28 | low | 28
Economic efficiency | Investment costs | Footprint requirement |  | 3 | low | 30 | low | 30 | low | 30 | low | 30 | low | 30 | low | 30
|  | Structural engineering |  | 4 | low (25-60 €/PT) | 11 | low (25-60 €/PT) | 11 | low | 32 | low | 32 | high (4000-8000 €/(m³/h)) | 12,13, 14,15 | high | 34
|  | Mechanical engineering |  | 5 |  |  |  |  | low | 34 | low | 32 |  |  | high | 34
|  | E+MCR technology |  | 6 |  |  |  |  | low | 34 | low | 32 |  |  | high | 34
| Operating costs | Personnel requirement / costs |  | 7 | low | 11 | low | 11 | low | 34 | low | 32 | medium (0.26-0.4 €/m³) | 12,13, 14,15 | high | 34
|  | Energy requirement / costs |  | 8 | low | 33 | low | 33 | low | 33 | low (~ 0.001 kWh/m³) | 5 |  |  | high (0.45-0.70 $/m³ desalination) | 10
|  | Disposal of residues |  | 9 | low | 11 | low | 11 | low | 34 | medium | 32 |  |  | high | 34
|  | Operating supplies (precipitant etc.) |  | 10 | low | 11 | low | 11 | low | 34 | medium | 32 |  |  | high | 34
|  | Preventive maintenance costs |  | 11 | medium | 11 | medium | 11 | medium | 34 | medium | 32 |  |  | high | 32
Effects on the environment through operation of the facility | CH4 emission |  |  | 12 | none | 30 | none | 30 | none | 30 | none | 30 | none | 30 | none | 30
| Odour nuisance |  |  | 13 | low | 27 | low | 27 | low | 27 | low | 30 | low | 30 | low | 30
| Sounds / noisiness |  |  | 14 | low | 27 | low | 27 | low | 27 | low | 30 | low | 30 | low | 30
| Aerosols |  |  | 15 | low | 27 | low | 27 | low | 27 | low | 30 | none | 30 | none | 30
| Insects (worms, flies, etc.) |  |  | 16 | medium | 27 | medium | 27 | medium | 27 | low | 30 | none | 30 | none | 30
Requirements on operating personnel | Operability /operational expenditure |  |  | 17 | medium | 31 | medium | 31 | medium | 31 | medium | 30 | high | 30 | high | 30
| Preventive maintenance expenditure |  |  | 18 | high | 31 | high | 31 | high | 31 | medium | 30 | high | 30 | high | 30
| Required training for operating personnel |  |  | 19 | high (trained personnel necessary) | 27 | high (trained personnel necessary) | 27 | high (trained personnel necessary) | 27 | high (trained personnel necessary) | 30 | high (trained personnel necessary) | 30 | high (trained personnel necessary) | 30
Plant technology | Degree of mechanization |  |  | 20 | low | 27 | medium | 27 | medium | 27 | low | 27 | high | 27 | high | 27
| Robustness |  |  | 21 | medium | 27 | medium | 27 | high | 27 | high | 27 | medium | 26 | medium | 27
| Process stability |  |  | 22 | high | 27 | high | 27 | high | 27 | high | 27 | high | 27 | high | 27
| Ability to influence the discharge quality operationally |  |  | 23 | high | 30 | high | 30 | high | 30 | high | 30 | high | 30 | high | 30
| Discharge quality (treatment performance) | COD / BOD elimination |  | 24 | low (> 20 % or < 40 mg/l ) | 11 | low (> 20 % or < 40 mg/l) | 11 | low (> 20 % or < 40 mg/l ) | 11 | low | 30 | high (with aeration ca. 89-96 % or COD < 30 mg/l, BOD < 5 mg/l) | 12,13, 14,15 | not relevant (post-treatment only) | 30
|  | SS reduction |  | 25 | medium / high (> 50 % or < 5 mg/l) | 11 | medium / high (> 50 % or < 5 mg/l) | 11 | medium / high (> 50 % or < 5 mg/l) | 11 | high | 30 | high (almost 100 %) | 12,13, 14,15 | high | 26
|  | Nutrient elimination | Ammonium | 26 | medium (< 5 mg/l) | 11 | medium (< 5 mg/l) | 11 | medium (< 5 mg/l) | 11 | low (ca. 10 %) | 3 | high (with aeration ca. 90 % or 0.1-2 mg/l) | 12,13, 14,15 | not relevant (post-treatment only) | 30
|  |  | Nitrate | 27 | high (< 10 mg/l) | 11 | high (< 10 mg/l) | 11 | high (< 10 mg/l) | 11 | no influence (0 %) | 3 | medium / high (4.5 mg/l) | 12,13, 14,15 | not relevant (post-treatment only) | 30
|  |  | Phosphorus | 28 | medium (30 % without flocculation) / high (ca. 70 % or < 0.3 mg/l with flocculation) | 11 | medium (30 % without flocculation) / high (ca. 70 % or < 0.3 mg/l with flocculation) | 11 | medium (30 % without flocculation) / high (ca. 70 % or < 0.3 mg/l with flocculation) | 11 | high | 3 | high (with precipitation ca. 90 % or 0.5-0.7 mg/l) | 12,13, 14,15 | not relevant (post-treatment only) | 30
|  | Reductions of pathogens | Viruses | 29 | medium (1 - 3 log steps) | 1 | medium (1 - 3 log steps) | 1 | medium (1 - 3 log steps) | 1 | medium (1 - 3 log steps) | 1 | high (2.5 - > 6 log steps) | 1 | high (2.5 - > 6 log steps) | 1
|  |  | Bacteria | 30 | medium (0 - 3 log steps) | 1 | medium (0 - 3 log steps) | 1 | medium (0 - 3 log steps) | 1 | low (0 - 1 log steps) | 1 | high (3.5 - > 6 log steps) | 1 | high (3.5 - >6 log steps) | 1
|  |  | Protozoa | 31 | medium (0 - 3 log steps) | 1 | medium (0 - 3 log steps) | 1 | medium (0 - 3 log steps) | 1 | medium (1 - 3 log steps) | 1 | high (> 6 log steps) | 1 | high (> 6 log steps) | 1
|  |  | Helminths | 32 | medium (1 - 3 log steps) | 1 | medium (1 - 3 log steps) | 1 | medium (1 - 3 log steps) | 1 | low (2 log steps) | 1 | high (> 3 log steps) | 1 | high (> 3 log steps) | 1
|  | Colour / odour |  | 33 | no influence | 30 | no influence | 30 | no influence | 30 | no influence | 30 | no influence | 30 | low (NF), medium / high (RO) | 35
|  | Residual turbidity |  | 34 | low | 11 | low | 11 | low | 11 | low | 3 | low | 34 | low | 30
|  | Salting up due to process |  | 35 | no influence | 30 | no influence | 30 | no influence | 30 | medium (salting-up due to precipitant chemicals) | 30 | medium (salting-up due to precipitant chemicals) | 34 | no influence (but heavily salted concentrate for disposal) | 30
| Accumulation of residues |  |  | 36 | low | 30 | low | 30 | low | 30 | low | 30 | low (550-1100 l/(PT·a) stabilised, fluid or 17-34 l/(PT·a) dewatered sludge) | 3 | medium (heavily salted concentrate for disposal) | 30
Irrigation technology | Root irrigation |  |  | 37 | suitable | 10 | suitable | 10 | suitable | 10 | suitable | 10 | suitable | 10 | suitable | 10
| Trickling irrigation |  |  | 38 | suitable (requires disinfection) | 35 | suitable (requires disinfection) | 35 | suitable (requires disinfection) | 35 | suitable (requires disinfection) | 35 | suitable | 10 | suitable | 10
| Sprinkler / spray systems |  |  | 39 | suitable (requires disinfection) | 35 | suitable (requires disinfection) | 35 | suitable (requires disinfection) | 35 | suitable (requires disinfection) | 35 | suitable | 10 | suitable | 10
| Flooding |  |  | 40 | suitable (requires disinfection) | 35 | suitable (requires disinfection) | 35 | suitable (requires disinfection) | 35 | suitable (requires disinfection) | 35 | suitable | 10 | suitable | 10
Types of usage | Agricultural irrigation |  |  | 41 | recommended (requires disinfection) | 35 | recommended (requires disinfection) | 35 | recommended (requires disinfection) | 35 | recommended (requires disinfection) | 35 | recommended | 30 | recommended | 30
| Process water (e.g., toilet flushing) |  |  | 42 | possible (requires disinfection) | 35 | possible (requires disinfection) | 35 | possible (requires disinfection) | 35 | possible (requires disinfection) | 35 | recommended | 30 | recommended | 30
| Inner-city usage (e.g., irrigation, water for fire-fighting) |  |  | 43 | possible (requires disinfection) | 35 | possible (requires disinfection) | 35 | possible (requires disinfection) | 35 | possible (requires disinfection) | 35 | recommended | 30 | recommended | 30
| Forestry irrigation |  |  | 44 | recommended | 27 | recommended | 27 | recommended | 27 | recommended | 30 | recommended | 30 | recommended | 30

## Disinfection
Aspect |  |  |  | Line No. | Disinfection
[5 empty] | Membrane (UF) |  | UV |  | Ozone |  | Soil filter |  | Polishing pond |  | Chlorine
Health risk | Operating personnel water processing facility |  |  | 1 | high (handling of chemicals) | 28 | medium | 26 | high (exposure to ozone) | 28 | low | 28 | low | 28 | high (handling of chemicals) | 28
| Users of reused water |  |  | 2 | low | 28 | low | 28 | low | 28 | low | 28 | medium (requires post-disinfection) | 26 | low (only where excess chlorine is applied) | 26
Economic efficiency | Investment costs | Footprint requirement |  | 3 | low | 30 | low | 30 | low | 30 | high | 30 | high | 30 | low | 30
|  | Structural engineering |  | 4 | high | 34 | low (7-41 €/PT) | 16 | high (0.52 €/m³) | 17 | high | 18,19,20,21 | low | 22,23 | low | 34
|  | Mechanical engineering |  | 5 | high | 34 | medium | 26 | high | 32 | low | 18,19,20,21 | low | 22,23 | medium (safety technology) | 26
|  | E+MCR technology |  | 6 | high | 34 | medium | 26 | high | 17 | low | 18,19,20,21 | low | 22,23 | low | 34
| Operating costs | Personnel requirement / costs |  | 7 | high (0.2-0.8 €/m3) | 7 | low (0.03-0.05 €/m3) | 7 | medium (0.05-0.2 €/m3) | 7 | low | 18,19,20,21 | low | 22,23 | low (0.04-0.06 €/m3) | 7
|  | Energy requirement / costs |  | 8 | [6 empty] | low | 18,19,20,21 | low | 22,23
|  | Disposal of residues |  | 9 | [6 empty] | low | 18,19,20,21 | low | 22,23
|  | Operating supplies (precipitant etc.) |  | 10 | [6 empty] | low | 18,19,20,21 | low | 22,23
|  | Preventive maintenance costs |  | 11 | [6 empty] | low | 18,19,20,21 | low | 22,23
Effects on the environment through operation of the facility | CH4 emission |  |  | 12 | none | 26 | none | 26 | none | 26 | none | 26 | small (possible methane formation with anaerobic degradation of residual loads and sludge) | 30 | none | 26
| Odour nuisance |  |  | 13 | low | 30 | low | 30 | low | 30 | low | 30 | low | 30 | low | 30
| Sounds / noisiness |  |  | 14 | low | 30 | none | 26 | low | 30 | none | 26 | none | 26 | none | 26
| Aerosols |  |  | 15 | none | 30 | none | 30 | none | 30 | low | 30 | low | 30 | none | 30
| Insects (worms, flies, etc.) |  |  | 16 | none | 30 | none | 30 | none | 30 | medium | 30 | high (mosquitos) | 30 | none | 30
Requirements on operating personnel | Operability /operational expenditure |  |  | 17 | high | 30 | low | 30 | high | 30 | low | 30 | low | 30 | high | 30
| Preventive maintenance expenditure |  |  | 18 | high | 30 | medium | 26 | high | 30 | low | 30 | low | 30 | high | 30
| Required training for operating personnel |  |  | 19 | high (trained personnel required) | 30 | medium | 26 | high (trained personnel required) | 30 | low | 30 | low | 30 | high (trained personnel required) | 30
Plant technology | Degree of mechanization |  |  | 20 | high | 27 | medium | 27 | medium | 27 | low | 27 | low | 27 | low | 27
| Robustness |  |  | 21 | medium | 27 | high | 27 | medium | 27 | medium | 26 | low / medium | 27 | medium | 26
| Process stability |  |  | 22 | high | 27 | high | 27 | high | 27 | high | 27 | medium / high | 26 | high | 27
| Ability to influence the discharge quality operationally |  |  | 23 | high | 30 | high | 30 | high | 30 | low | 30 | low | 30 | high | 30
| Discharge quality (treatment performance) | COD / BOD elimination |  | 24 | not relevant (for post treatment only) | 30 | no influence | 34 | not relevant (for post treatment only) | 30 | high (ca. 85 %) | 18,19,20,21 | low (reduction residual loads / balancing of effluent peaks) | 26 | no influence | 34
|  | SS reduction |  | 25 | high | 26 | no influence | 34 | not relevant (for post treatment only) | 30 | high (ca. 90 %) | 18,19,20,21 | low (ditto) | 26 | no influence | 34
|  | Nutrient elimination | Ammonium | 26 | not relevant (for post treatment only) | 26 | no influence | 34 | not relevant (for post treatment only) | 30 | high (ca. 80 %) | 18,19,20,21 | low (ditto) | 26 | no influence | 34
|  |  | Nitrate | 27 | not relevant (for post treatment only) | 26 | no influence | 34 | not relevant (for post treatment only) | 30 | low (10 % unplanted) / high (70 % unplanted) | 18,19,20,21 | low (ditto) | 26 | no influence | 34
|  |  | Phosphorus | 28 | not relevant (for post treatment only) | 26 | no influence | 34 | not relevant (for post treatment only) | 30 | medium (ca. 30 % unplanted) / high (ca. 80 % unplanted) performance sinks however with operating time | 18,19,20,21 | low (reduction residual loads / balancing of effluent peaks) | 26 | no influence | 34
|  | Reductions of pathogens | Viruses | 29 | high (2.5 - > 6 log step) | 1 | medium (1 - > 3 log steps) | 1 | high (3 - 6 log steps) | 1 | medium / low (1.5 - 2.5 log steps) | 18.19.20,21 | high (1 - 4 log steps) | 1 | medium (1 - 3 log steps) | 1
|  |  | Bacteria | 30 | high (3.5 - > 6 log step) | 1 | high (2 - > 4 log steps) | 1 | high (2 - 6 log steps) | 1 | medium / low (1,5 - 2,5 log steps) | 18,19,20,21 | high (1 - 6 log steps) | 1 | high (2 - 6 log steps) | 1
|  |  | Protozoa | 31 | high (> 6 log step) | 1 | high (> 3 log steps) | 1 | low (1 - 2 log steps) | 1 | medium / low (1.5 - 2,5 log steps) | 18,19,20,21 | high (1 - 4 log steps) | 1 | low (0 - 1.5 log steps) | 1
|  |  | Helminths | 32 | high (> 3 log step) | 1 | no influence | 1 | low (0 - 2 log steps) | 1 | medium | 26 | medium (1 - 3 log steps) | 1 | low (0 - < 1 log steps) | 1
|  | Colour / odour |  | 33 | no influence | 30 | low (decolouration possible) | 30 | low (removal of colour and odour substances) | 30 | medium (repossible formation of odour substances with anaerobic conditions) | 30 | medium (possible colouration due to algae; odour formation with anaerobic conditions) | 30 | medium (aggravation of odour and taste if residual chlorine contained in water) | 30
|  | Residual turbidity |  | 34 | low | 34 | no influence | 34 | no influence | 34 | low | 18,19,20,21 | medium | 30 | no influence | 34
|  | Salting up due to process |  | 35 | no influence | 30 | no influence | 30 | no influence | 30 | no influence | 30 | small (danger of salting up through water evaporation during longer retention times, stronger sunlight exposure, larger water surface) | 30 | low | 26
| Accumulation of residues |  |  | 36 | low (concentrate for disposal) | 30 | none | 30 | none | 30 | low | 26 | low (periodic sludge clearance) | 30 | none | 30
Irrigation technology | Root irrigation |  |  | 37 | suitable | [8 empty] | 10 | not suitable | 36
| Trickling irrigation |  |  | 38 | suitable | [8 empty] | 10 | not suitable | 36
| Sprinkler / spray systems |  |  | 39 | suitable | [8 empty] | 10 | not suitable | 36
| Flooding |  |  | 40 | suitable | [8 empty] | 10 | not suitable | 36
Types of usage | Agricultural irrigation |  |  | 41 | recommended | [8 empty] | 30 | possible | 36
| Process water (e.g., toilet flushing) |  |  | 42 | recommended | [8 empty] | 30 | recommended | 30
| Inner-city usage (e.g., irrigation, water for fire-fighting) |  |  | 43 | recommended | [8 empty] | 30 | possible | 36
| Forestry irrigation |  |  | 44 | recommended | [8 empty] | 30 | not suitable | 36

## Legende
Nr. | Quelle | Quelle
1 | WHO, 2006a | WHO - World Health Organization (2006): Guidelines for the safe use of wastewater, excreta and greywater, Volume 2: Wastewater use in agriculture, World Health Organization, Geneva, 2006, ISBN: 92-4-154683-2
2 | Günthert und Reicherter, 2001 | Günthert, F.W.; Reicherter, E. (2001): Investitionskosten der Abwasserreinigung, Oldenbourg Industrieverlag GmbH, ISBN 3486265075
3 | ATV-DVWK, 2000 | ATV-DVWK-A 131 (2000): Bemessung von einstufigen Belebungsanlagen, Ausgabe: Mai 2000, Deutsche Vereinigung für Wasserwirtschaft, Abwasser und Abfall e.V., Hennef
4 | DWA Landesverband Bayern, 2005 | DWA Landesverband Bayern (2005): Kanal- und Kläranlagennachbarschaften, Fortbildung des Betriebspersonals 2005, München, ISBN 3887210581
5 | MURL, 1999 | MURL - Ministerium für Umwelt, Raumordnung und Landwirtschaft des Landes NRW (1999): Handbuch - Energie in Kläranlagen, Düsseldorf, September 1999
6 | Von Sperling und Chernicharo, 2006 | Von Sperling, M.; Chernicharo, C.A.L. (2006): Wastewater treatment in warm climates, Water 21, April 2006
7 | ATV, 1998 | ATV-M 205 (1998): Desinfektion von biologisch gereinigtem Abwasser, Ausgabe Juli 1998, Deutsche Vereinigung für Wasserwirtschaft, Abwasser und Abfall e. V., Hennef
8 | Grünebaum und Weyand, 1995 | Grünebaum, T.; Weyand, M. (1995): Reduzierung der Betriebskosten bei der Abwasserbehandlung, 47. Darmstädter Seminar - Abwassertechnik - am 15. November 1995, Schriftenreihe WAR, Band 86, TH Darmstadt, ISBN 3-923419791, S. 155-178
9 | Lenz, 2004 | Lenz, G. (2004): Qualifikation des Betriebspersonals auf Kläranlagen, Hrsg.: Deutsche Vereinigung für Wasserwirtschaft, Abwasser und Abfall e. V., Hennef
10 | Alcalde et al., 2004 | Alcalde, L.; Oron G.; Manor, Y.; Gillerman, L.; Salgot, M.(2004): Wastewater Reclamation and reuse for agricultural irrigation in arid regions: The experience of the city of Arad, Israel, Israeli-Palesinian International Conference on Water for Life, Antalya, Turkey, Oct. 2004, www.ipcri.org
11 | Strohmeier, 1998 | Strohmeier, A. (1998): Filtrationsanlagen, Kommunale Kläranlage, Technische Akademie Esslingen, Expert Verlag, ISBN 3816914063, S. 246-266
12 | Wedi, 2005 | Wedi, D.; Wild, W.; Resch, H. (2005): Betriebsergebnisse der MBR Monheim - Abwasserreinigung und Erhalt der Permeabilitäten mittels chlorfreier chemischer Reinigung, in: Membrantechnik in der Wasseraufbereitung und Abwasserbehandlung - Perspektiven, Neuentwicklungen und Betriebserfahrungen im In- und Ausland, 6. Aachener Tagung Siedlungswasserwirtschaft und Verfahrenstechnik, Aachen 2005, Beitrag A9, Hrsg.: T. Melin, J. Pinnekamp, M. Dohmann, ISBN 3 86130-775-8
13 | Engelhardt, 2006 | Engelhardt, N. (2006): Die Membranbelebungsanlage Nordkanal, Wiener Mitteilungen, Band 195, Betriebserfahrungen moderner Kläranlagen, ISBN 3852340861
14 | Günder, 2001 | Günder, B. (2001): Das Membranbelebungsverfahren in der kommunalen Abwasserbehandlung, Kommunale Kläranlagen, 2. Auflage, Technische Akademie Esslingen, Expert Verlag, ISBN 3816919944, S. 173-192
15 | Frechen, 2006 | Frechen, F. B. (2006): Leistung und Kosten des Membranbelebungsverfahrens, DWA WasserWirtschafts-Kurs M/2 vom 11.-13. Oktober 2006, ISBN 3-939057584
16 | Schleypen, 2005 | Schleypen, P. (2005): Isar-Badegewässerqualität, Vortrag beim Wasserwirtschaftlichen Kolloquium an der Universität der Bundeswehr München
17 | Cornel, 2006 | Cornel, P. (2006): Weitergehende Behandlung von Kläranlagenabläufen (A-Kohle, Oxidations-, Desinfektionsverfahren u. a.), DWA WasserWirtschafts-Kurs M 2 vom 11.-13. Oktober 2006, ISBN 3-939057584
18 | Laber, 2001 | Laber, J. (2001): Bepflanzte Bodenfilter zur weitergehenden Reinigung von Oberflächenwasser und Kläranlagenabläufen, Wiener Mitteilungen, Band 167, ISBN 3-85234-058-6
19 | Novak, 2005 | Nowak, J. (2005): Abwasserbehandlung in bepflanzten Bodenfiltern – Arbeitsblatt DWA-A 262 (Bemessung, Bau und Betrieb), 2005, DWA WasserWirtschafts-Kurs L/6 Abwasserentsorgung im ländlichen Raum, ISBN 3 939057002
20 | DWA, 2006 | DWA-A 262 (2006): Grundsätze für Bemessung, Bau und Betrieb von Pflanzenkläranlagen mit bepflanzten Bodenfiltern zur Reinigung kommunalen Abwassers, Ausgabe: März 2006, Deutsche Vereinigung für Wasserwirtschaft, Abwasser und Abfall e. V., Hennef
21 | Lützner, 2002 | Lützner, K. (2002): Ein Beitrag zur Bilanzierung von Bodenfiltern, Dresdner Berichte 21, TU Dresden, ISSN 1615083X
22 | IRC, 2004 | IRC - International Water and Sanitation Centre (2004): Waste stabilization ponds for wastewater treatment, http://www.irc.nl/page/8237
23 | Ruhrverband, 1992 | Ruhrverband (1992): Seminar über Schönungsteiche am 19. November 1992 beim Ruhrverband in Essen
24 | Barjenbruch und Al Jiroudi, 2005 | Barjenbruch M.; Al Jiroudi D. (2005): Erfahrungen aus dem Vergleich von Kleinkläranlagen auf dem Demonstrationsfeld in Dorf Mecklenburg, GWF Wasser Abwasser, Jg. 146, Nr. 5, 2005, S. 400-407
37 | Tilley et al., 2014 | Tilley et al. (2014): Tilley, E., Ulrich, L., Lüthi, C., Reymond, Ph., Schertenleib, R. and Zurbrügg, C., 2014. Compendium of Sanitation Systems and Technologies. 2nd Revised Edition. Swiss Federal Institute of Aquatic Science and Technology (Eawag). Dübendorf, Switzerland
38 | Reynaud und Buckley, 2016 | Reynaud, N. & Buckley, C. (2016): The anaerobic baffled reactor (ABR) treating communal wastewater under mesophilic conditions: a review. Water Science & Technology 73 (3)
39 | Foxon, 2009 | Foxon, K.M. (2009): Analysis of a pilot-scale anaerobic baffled reactor treating domestic wastewater. PhD Thesis, University of KwaZulu-Natal, Durban.
40 | Reynaud und Buckley, 2015 | Reynaud, N. & Buckley, C., (2015): Field-data on parameters relevant for design, operation and monitoring of communal Decentralized Wastewater Treatment Systems (DEWATS). Water Practice & Technology 10 (4)
25 | Arbeitsgruppe gemeinsam
26 | Tim Fuhrmann (persönliche Bewertung)
27 | Hans Huber (persönliche Bewertung)
28 | Volker Karl (persönliche Bewertung)
29 | Roland Knitschky (persönliche Bewertung)
30 | Alessandro Meda und Peter Cornel (persönliche Bewertung)
31 | Hermann Orth (persönliche Bewertung)
32 | Holger Scheer (persönliche Bewertung)
33 | Florian Schmidtlein (persönliche Bewertung)
34 | Christina Schwarz (persönliche Bewertung)
35 | Josef Lahnsteiner (persönliche Bewertung)
36 | Horst Reinhardt (persönliche Bewertung)
41 | Andreas Schmidt (persönliche Bewertung)